## Specification_EN_English
| WVLVS-IP54-6KW | WVLVS-IP54-8KW | WVLVS-IP54-12KW
PV (DC Input)
Recommended max. PV input power | 8000W | 16000W | 16000W
Max. input voltage (Voc) | 500V
MPPT operating voltage range | 85V-450V (@85V start up)
Number of MPPT | 1 | 2 | 2
Max. number of input strings per MPPT | 2 | 2 | 2
Max. input current per MPPT | 27A | 27/27A (MAX:54A) | 27/27A (MAX:54A)
Max. short-circuit current per MPPT | 35A | 32A/32A | 32A/32A
Grid (AC Input)
Max. input power | 11500W | 14950W | 20700W
Max. input current | 50A | 65A | 90A
Rated grid voltage | 220/230/240Vac
Rated grid frequency | 50/60Hz
Acceptable range | 170-280Vac (For UPS); 90-280Vac (For Home Appliances)
Generator (AC Input)
Max. input power | / | 11500W | 12000W
Rated input voltage/frequency | / | 220/230/240V, 45-65Hz | 230V, 50/60Hz
Max. generator input current | / | 50A | 70A
Battery parameters (Bidirection)
Battery type | LiFePO4 / Lead-acid
Battery voltage range | 40~60Vdc
Rated battery voltage | 48Vdc | 48Vdc | 48Vdc
Max. charge/discharge current | 120A/130A | 160A/180A | 210A/230A
BMS communication mode | RS485 | RS485/CAN | RS485
Back-up Output (AC Output)
Rated output power | 6000W/6000VA (Dural outputs) | 8000W/8000VA (Dural outputs) | 12000W/12000VA (Dural outputs)
Rated output current | 27.3A | 36.4A | 54.5A
Rated output voltage/Frequency | 220/230/240Vac 50/60Hz
Parallel Capacity | Single-phase Max. 12 units; Three-phase Max. 12 units | Single-phase Max. 9 units; Three-phase Max. 12 units | Single-phase Max. 6 units; Three-phase Max. 12 units
Surge power | 12000VA 5s | 16000VA 5s | 24000VA 5s
THDv (@ linear load) | <3% | <3% | <3%
Switching time | 10ms typical (For UPS); 20ms typical (For Home Appliances)
Efficiency
Peak efficiency | 98% | 98% | 98%
Max. MPPT efficiency | 99.9% | 99.9% | 99.9%
Protection
Inner protection | Output short-circuit protection; Output overvoltage protection
Surge protection | PV: Type III, AC: Type III
IP rating | IP54
General Parameters
Operating temperature range | -10°C~55°C
Relative humidity range | 5%~95% | 10%~95% | 10%~95%
Max. operating altitude | >2000m derating
Standby self-consumption | <10W | <20W | <20W
Installation type | Wall-mounted
Cooling mode | Fan cooling
Communication | RS232/RS485/Dry contact/WI-FI
Display | LCD
Mechanical Specifications
Inverter dimensions (L*W*H) | 445*347*120mm | 520*420*125mm | 630*525*125mm
Net weight | 12.4kg | 17.5kg | 28.5kg
Carton dimensions (L*W*H) | 560*465*240mm | / | /
Gross weight | 14.6kg | / | /
Warranty period | 5 Years (3-Year Replacement & 2-Year Repair)

## Specification_EN_English (2)
| WVLVS-IP54-6KW | WVLVS-IP54-8KW | WVLVS-IP54-12KW
PV (DC Input)
Recommended max. PV input power | 8000W | 16000W | 16000W
Max. input voltage (Voc) | 500V | 500V | 500V
MPPT operating voltage range | 85V-450V (@85V start up) | 85V-450V (@85V start up) | 85V-450V (@85V start up)
Number of MPPT | 1 | 2 | 2
Max. number of input strings per MPPT | 2 | 2 | 2
Max. input current per MPPT | 27A | 27/27A (MAX:54A) | 27/27A (MAX:54A)
Max. short-circuit current per MPPT | 35A | 32A/32A | 32A/32A
Grid (AC Input)
Max. input power | 11500W | 14950W | 20700W
Max. input current | 50A | 65A | 90A
Rated grid voltage | 220/230/240Vac | 220/230/240Vac | 220/230/240Vac
Rated grid frequency | 50/60Hz | 50/60Hz | 50/60Hz
Acceptable range | 170-280Vac; 90-280Vac | 170-280Vac; 90-280Vac | 170-280Vac; 90-280Vac
Generator (AC Input)
Max. input power | / | 11500W | 12000W
Rated input voltage/frequency | / | 220/230/240V, 45-65Hz | 230V, 50/60Hz
Max. generator input current | / | 50A | 70A
Battery parameters (Bidirection)
Battery type | LiFePO4 / Lead-acid | LiFePO4 / Lead-acid | LiFePO4 / Lead-acid
Battery voltage range | 40~60Vdc | 40~60Vdc | 40~60Vdc
Rated battery voltage | 48Vdc | 48Vdc | 48Vdc
Max. charge/discharge current | 120A/130A | 160A/180A | 210A/230A
BMS communication mode | RS485 | RS485/CAN | RS485
Back-up Output (AC Output)
Rated output power | 6000W/6000VA (Dural outputs) | 8000W/8000VA (Dural outputs) | 12000W/12000VA (Dural outputs)
Rated output current | 27.3A | 36.4A | 54.5A
Rated output voltage/Frequency | 220/230/240Vac 50/60Hz | 220/230/240Vac 50/60Hz | 220/230/240Vac 50/60Hz
Parallel Capacity | Single-phase Max. 12 units; Three-phase Max. 12 units | Single-phase Max. 9 units; Three-phase Max. 12 units | Single-phase Max. 6 units; Three-phase Max. 12 units
Surge power | 12000VA 5s | 16000VA 5s | 24000VA 5s
THDv (@ linear load) | <3% | <3% | <3%
Switching time | 10ms typical; 20ms typical | 10ms typical; 20ms typical | 10ms typical; 20ms typical
Efficiency
Peak efficiency | 98% | 98% | 98%
Max. MPPT efficiency | 99.9% | 99.9% | 99.9%
Protection
Inner protection | Output short-circuit protection; Output overvoltage protection | Output short-circuit protection; Output overvoltage protection | Output short-circuit protection; Output overvoltage protection
Surge protection | PV: Type III, AC: Type III | PV: Type III, AC: Type III | PV: Type III, AC: Type III
IP rating | IP54 | IP54 | IP54
General Parameters
Operating temperature range | -10°C~55°C | -10°C~55°C | -10°C~55°C
Relative humidity range | 5%~95% | 10%~95% | 10%~95%
Max. operating altitude | >2000m derating | >2000m derating | >2000m derating
Standby self-consumption | <10W | <20W | <20W
Installation type | Wall-mounted | Wall-mounted | Wall-mounted
Cooling mode | Fan cooling | Fan cooling | Fan cooling
Communication | RS232/RS485/Dry contact/WI-FI | RS232/RS485/Dry contact/WI-FI | RS232/RS485/Dry contact/WI-FI
Display | LCD | LCD | LCD
Mechanical Specifications
Inverter dimensions (L*W*H) | 445*347*120mm | 520*420*125mm | 630*525*125mm
Net weight | 12.4kg | 17.5kg | 28.5kg
Carton dimensions (L*W*H) | 560*465*240mm | / | /
Gross weight | 14.6kg | / | /
Warranty period | 3-Year Replacement & 2-Year Repair | 3-Year Replacement & 2-Year Repair | 3-Year Replacement & 2-Year Repair